## Slide 1: SAHV Annual Review…
Overview of Changes.

## Slide 2: Section 2 Changes
Definition of “Disconnection Point”
Change = Removal of the word “total”.
Disconnection Point – An adequate break created by the total removal or absence of Conductors and deemed no longer a source of inadvertent energisation. The break Shall:-
  not be able to be re-established by normal Switching operations, and
  maintain Exclusion Zone appropriate to the voltage or maintain electrical non-flashover distance appropriate to the voltage as defined by the Electricity Entity, and
  be created in accordance with an Approved Procedure to establish a Disconnection Point
Operational Effect:
When it is not possible or practical to totally remove conductors (e.g. large bridges on 110kV towers) a break may be classed as adequate under the definition if all the dot points are met.
** This change mostly applies for Powerlink. Energex’s policy is that by default the conductor is totally removed to provide the break. Only under limited circumstances will the exception be allowed.
Section 2 Changes

## Slide 3: Section 2 Changes
Definition of “Not Electrically Connected”
Change = Removal of the word “total”.
  Not Electrically Connected – Electrical Apparatus Disconnected from all sources of Supply by the total removal or absence of Conductors, appropriate to the voltage and insulating medium and, not able to be Energised by Switching and identified in accordance with an Approved Procedure
Operational Effect:
When it is not possible or practical to totally remove conductors (e.g. large bridges on 110kV towers) a break may be classed as adequate under the definition if the conditions in this definition AND all the dot points in the definition of Disconnection point are met.
** This change mostly applies for Powerlink. Energex’s policy is that by default the conductor is totally removed to provide the break. Only under limited circumstances will the exception be allowed.

## Slide 4
Changing Isolation Points on an Permit (4.1)
Change = Insert: “…prior to isolation points being altered…”
  If Isolation Points change during the course of work, under an Access / Test Permit, then prior to Isolation Points being altered, all current related Access/Test Permits Shall be Surrendered and cancelled and new Access/Test Permits issued reflecting the new Isolation Points.
Operational Effect:
  No real effect – this is just a more specific wording to remove ambiguity.
  See also addition of similar paragraph to Section 5.3 regarding changing location of Operator Earths.
Section 4 Changes

## Slide 5
Earthing Requirements when Issuing Permits (5.3)
Change = Alteration of wording : “…a minimum of one set of Operator Earths shall be applied…”
  Operator Earths Shall be applied to ensure Electrical Apparatus in the area where a Work Area is or can be established is Earthed prior to the issue of an Access / Test Permit.
Operational Effect:
  Reduced poor wording and ambiguity regarding the number of earths required when issuing a permit.
  Sufficient Earths to adequately earth the work area is the minimum number required. It may be one – it may be more.
Section 5 Changes

## Slide 6
Requirement for Recipient to Remain on Site while TP is on Issue. (9.3)
Change = Removal of wording: “A test permit should not remain on issue (e.g. overnight) unless the Recipient is in attendance.”
Operational Effect:
  This restriction had no practical or safety benefit and actually created inefficiencies.
  A crew may now sign off a TP, leave the site, then return the next day and sign back on (as we currently do with an AP) provided all necessary checks are made to ensure the safety of the workgroup.
Section 9 Changes

## Slide 7
Section 9 Changes
Responsibilities of Switching Coordinator when Suspending Permit. (9.16 & 9.17)
Change = Insert new c) in 9.16: (old c now = d, old d now = e, old e moved to S9.17))
  “c) before approval is granted, the Switching Co-ordinator Shall:-
    i) check if other work groups will be affected and advise affected Recipient/s to suspend or surrender their Access Permits
    ii) confirm with affected Recipient/s that their Access Permits have been suspended or surrendered and cancelled
    iii) confirm the status of the Electrical Apparatus at the time of the suspension of the work
    iv) cancel any surrendered Access.”
Operational Effect:
No real effect – more clearly outlines the responsibilities of the Recipient and Switching Coordinator and lists the responsibilities in a more naturally sequential order.

## Slide 8
Section 9 Changes
Minor Wording Changes Throughout…
  Definition of “Entity” – Now aligns with Electricity Act.
  Definition of “Should” removed due to conflicting legislative interpretations.
  All occurrences of “should” replaced with “shall” or “it is preferable to” as applicable.
  Document review period changed from one to two years.